## Shapes
W-SHAPES (Wide Flange) — AISC
Designation | d (in) | bf (in) | tw (in) | tf (in) | Wt (lb/ft) | Area (in²) | Notes
W4x13 | 4.16 | 4.06 | 0.28 | 0.345 | 13 | 3.83
W5x16 | 5.01 | 5 | 0.24 | 0.36 | 16 | 4.71
W6x9 | 5.9 | 3.94 | 0.17 | 0.215 | 9 | 2.68
W6x15 | 5.99 | 5.99 | 0.23 | 0.26 | 15 | 4.43
W6x20 | 6.2 | 6.02 | 0.26 | 0.365 | 20 | 5.87
W8x10 | 7.89 | 3.94 | 0.17 | 0.205 | 10 | 2.96
W8x18 | 8.14 | 5.25 | 0.23 | 0.33 | 18 | 5.26
W8x24 | 7.93 | 6.495 | 0.245 | 0.4 | 24 | 7.08
W8x31 | 8 | 7.995 | 0.285 | 0.435 | 31 | 9.13
W10x22 | 10.17 | 5.75 | 0.24 | 0.36 | 22 | 6.49
W10x33 | 9.73 | 7.96 | 0.29 | 0.435 | 33 | 9.71
W10x49 | 10 | 10 | 0.34 | 0.56 | 49 | 14.4
W12x16 | 11.99 | 3.99 | 0.22 | 0.265 | 16 | 4.71
W12x26 | 12.22 | 6.49 | 0.23 | 0.38 | 26 | 7.65
W12x40 | 11.94 | 8.01 | 0.295 | 0.515 | 40 | 11.8
W12x53 | 12.06 | 9.995 | 0.345 | 0.575 | 53 | 15.6
W12x72 | 12.25 | 12.04 | 0.43 | 0.67 | 72 | 21.1
W12x96 | 12.71 | 12.16 | 0.55 | 0.9 | 96 | 28.2
W14x22 | 13.74 | 5 | 0.23 | 0.335 | 22 | 6.49
W14x38 | 14.1 | 6.77 | 0.31 | 0.515 | 38 | 11.2
W14x53 | 13.92 | 8.06 | 0.37 | 0.66 | 53 | 15.6
W16x26 | 15.69 | 5.5 | 0.25 | 0.345 | 26 | 7.68
W16x36 | 15.86 | 6.985 | 0.295 | 0.43 | 36 | 10.6
W18x35 | 17.7 | 6 | 0.3 | 0.425 | 35 | 10.3
W18x46 | 18.06 | 6.06 | 0.36 | 0.605 | 46 | 13.5
C-SHAPES (American Standard Channels)
Designation | d (in) | bf (in) | tw (in) | tf (in) | Wt (lb/ft) | Area (in²)
C3x4.1 | 3 | 1.41 | 0.17 | 0.273 | 4.1 | 1.21
C4x5.4 | 4 | 1.58 | 0.184 | 0.296 | 5.4 | 1.59
C5x6.7 | 5 | 1.75 | 0.19 | 0.32 | 6.7 | 1.97
C6x8.2 | 6 | 1.92 | 0.2 | 0.343 | 8.2 | 2.4
C6x10.5 | 6 | 2.034 | 0.314 | 0.343 | 10.5 | 3.09
C7x9.8 | 7 | 2.09 | 0.21 | 0.366 | 9.8 | 2.87
C8x11.5 | 8 | 2.26 | 0.22 | 0.39 | 11.5 | 3.38
C8x13.75 | 8 | 2.343 | 0.303 | 0.39 | 13.75 | 4.04
C9x15 | 9 | 2.485 | 0.285 | 0.413 | 15 | 4.41
C10x15.3 | 10 | 2.6 | 0.24 | 0.436 | 15.3 | 4.49
C10x20 | 10 | 2.739 | 0.379 | 0.436 | 20 | 5.88
C12x20.7 | 12 | 2.942 | 0.282 | 0.501 | 20.7 | 6.09
C12x25 | 12 | 3.047 | 0.387 | 0.501 | 25 | 7.35
C15x33.9 | 15 | 3.4 | 0.4 | 0.65 | 33.9 | 9.96
C15x50 | 15 | 3.716 | 0.716 | 0.65 | 50 | 14.7
ANGLES (Equal & Unequal Leg)
Designation | Leg A (in) | Leg B (in) | Thickness (in) | Wt (lb/ft) | Area (in²)
L2x2x1/4 | 2 | 2 | 0.25 | 3.19 | 0.938
L2x2x3/8 | 2 | 2 | 0.375 | 4.7 | 1.36
L2.5x2.5x1/4 | 2.5 | 2.5 | 0.25 | 4.1 | 1.19
L3x3x3/16 | 3 | 3 | 0.1875 | 3.71 | 1.09
L3x3x1/4 | 3 | 3 | 0.25 | 4.9 | 1.44
L3x3x3/8 | 3 | 3 | 0.375 | 7.2 | 2.11
L3x3x1/2 | 3 | 3 | 0.5 | 9.4 | 2.75
L4x4x1/4 | 4 | 4 | 0.25 | 6.6 | 1.94
L4x4x3/8 | 4 | 4 | 0.375 | 9.8 | 2.86
L4x4x1/2 | 4 | 4 | 0.5 | 12.8 | 3.75
L5x5x3/8 | 5 | 5 | 0.375 | 12.3 | 3.61
L5x5x1/2 | 5 | 5 | 0.5 | 16.2 | 4.75
L6x6x3/8 | 6 | 6 | 0.375 | 14.9 | 4.36
L6x6x1/2 | 6 | 6 | 0.5 | 19.6 | 5.75
L3x2x1/4 | 3 | 2 | 0.25 | 3.92 | 1.15
L4x3x1/4 | 4 | 3 | 0.25 | 5.8 | 1.69
L4x3x3/8 | 4 | 3 | 0.375 | 8.5 | 2.48
L5x3x1/4 | 5 | 3 | 0.25 | 6.6 | 1.94
L6x4x3/8 | 6 | 4 | 0.375 | 12.3 | 3.61
L6x4x1/2 | 6 | 4 | 0.5 | 16.2 | 4.75
HSS (Hollow Structural Sections — Square & Rectangular)
Designation | H (in) | B (in) | Wall t (in) | Wt (lb/ft) | Area (in²)
HSS2x2x3/16 | 2 | 2 | 0.174 | 4.32 | 1.27
HSS2x2x1/4 | 2 | 2 | 0.233 | 5.41 | 1.59
HSS3x3x3/16 | 3 | 3 | 0.174 | 6.87 | 2.02
HSS3x3x1/4 | 3 | 3 | 0.233 | 8.81 | 2.59
HSS4x4x1/4 | 4 | 4 | 0.233 | 12.2 | 3.59
HSS4x4x3/8 | 4 | 4 | 0.349 | 17.3 | 5.08
HSS4x4x1/2 | 4 | 4 | 0.465 | 22.4 | 6.59
HSS5x5x1/4 | 5 | 5 | 0.233 | 15.6 | 4.59
HSS5x5x3/8 | 5 | 5 | 0.349 | 22.4 | 6.58
HSS6x6x1/4 | 6 | 6 | 0.233 | 19 | 5.59
HSS6x6x3/8 | 6 | 6 | 0.349 | 27.5 | 8.08
HSS6x6x1/2 | 6 | 6 | 0.465 | 35.1 | 10.3
HSS8x8x3/8 | 8 | 8 | 0.349 | 37.7 | 11.1
HSS8x8x1/2 | 8 | 8 | 0.465 | 48.9 | 14.4
HSS4x2x3/16 | 4 | 2 | 0.174 | 5.59 | 1.64
HSS4x3x1/4 | 4 | 3 | 0.233 | 10.5 | 3.09
HSS6x4x1/4 | 6 | 4 | 0.233 | 15.6 | 4.59
HSS6x4x3/8 | 6 | 4 | 0.349 | 22.4 | 6.59
HSS8x4x3/8 | 8 | 4 | 0.349 | 27.5 | 8.08
HSS8x6x3/8 | 8 | 6 | 0.349 | 32.6 | 9.59

## Plate
PLATE THICKNESS REFERENCE (Wt/sq ft = thickness × 40.8)
Thickness | Decimal (in) | Wt (lb/ft²) | Common Stock (in)
3/16 | 0.1875 | 7.65 | 48x96, 60x120
1/4 | 0.25 | 10.2 | 48x96, 60x120, 72x120
5/16 | 0.3125 | 12.75 | 48x96, 60x120
3/8 | 0.375 | 15.3 | 48x96, 60x120, 72x120
1/2 | 0.5 | 20.4 | 48x96, 60x120, 72x144
5/8 | 0.625 | 25.5 | 48x96, 60x120
3/4 | 0.75 | 30.6 | 48x96, 60x120, 72x120
1 | 1 | 40.8 | 48x96, 60x120
1-1/4 | 1.25 | 51 | 48x96, 60x120
1-1/2 | 1.5 | 61.2 | 48x96, 60x120
2 | 2 | 81.6 | 48x96, 60x96
PLATE WEIGHT CALCULATOR (Yellow = input, Green = result)
Thickness (dec in): | 0.25 | Length (in): | 48 | Width (in): | 96
Weight (lbs): |  | Formula: t × 40.8 × (L/12) × (W/12)
FLAT BAR REFERENCE (Wt = W × T × 3.4 lb/ft/in²)
Size (W x T) | Width (in) | Thickness (in) | Wt (lb/ft)
1 x 1/4 | 1 | 0.25 | 0.85
1 x 3/8 | 1 | 0.375 | 1.28
1 x 1/2 | 1 | 0.5 | 1.7
1-1/2 x 1/4 | 1.5 | 0.25 | 1.28
1-1/2 x 3/8 | 1.5 | 0.375 | 1.91
1-1/2 x 1/2 | 1.5 | 0.5 | 2.55
2 x 1/4 | 2 | 0.25 | 1.7
2 x 3/8 | 2 | 0.375 | 2.55
2 x 1/2 | 2 | 0.5 | 3.4
2 x 3/4 | 2 | 0.75 | 5.1
2-1/2 x 1/4 | 2.5 | 0.25 | 2.13
2-1/2 x 3/8 | 2.5 | 0.375 | 3.19
2-1/2 x 1/2 | 2.5 | 0.5 | 4.25
3 x 1/4 | 3 | 0.25 | 2.55
3 x 3/8 | 3 | 0.375 | 3.83
3 x 1/2 | 3 | 0.5 | 5.1
3 x 3/4 | 3 | 0.75 | 7.65
4 x 1/4 | 4 | 0.25 | 3.4
4 x 3/8 | 4 | 0.375 | 5.1
4 x 1/2 | 4 | 0.5 | 6.8
4 x 3/4 | 4 | 0.75 | 10.2
4 x 1 | 4 | 1 | 13.6
6 x 1/2 | 6 | 0.5 | 10.2
6 x 3/4 | 6 | 0.75 | 15.3
6 x 1 | 6 | 1 | 20.4

## Pipe
PIPE SIZE & WEIGHT REFERENCE (ASME B36.10)
NPS (in) | OD (in) | SCH40 Wall | SCH40 ID | SCH40 Wt/ft | SCH80 Wall | SCH80 ID | SCH80 Wt/ft | Material | Notes
1/2 | 0.84 | 0.109 | 0.622 | 0.85 | 0.147 | 0.546 | 1.09 | A53-B / A106-B
3/4 | 1.05 | 0.113 | 0.824 | 1.13 | 0.154 | 0.742 | 1.47 | A53-B / A106-B
1 | 1.315 | 0.133 | 1.049 | 1.68 | 0.179 | 0.957 | 2.17 | A53-B / A106-B
1-1/4 | 1.66 | 0.14 | 1.38 | 2.27 | 0.191 | 1.278 | 3 | A53-B / A106-B
1-1/2 | 1.9 | 0.145 | 1.61 | 2.72 | 0.2 | 1.5 | 3.63 | A53-B / A106-B | Common handrail
2 | 2.375 | 0.154 | 2.067 | 3.65 | 0.218 | 1.939 | 5.02 | A53-B / A106-B | Common support
2-1/2 | 2.875 | 0.203 | 2.469 | 5.79 | 0.276 | 2.323 | 7.66 | A53-B / A106-B
3 | 3.5 | 0.216 | 3.068 | 7.58 | 0.3 | 2.9 | 10.25 | A53-B / A106-B
3-1/2 | 4 | 0.226 | 3.548 | 9.11 | 0.318 | 3.364 | 12.5 | A53-B / A106-B
4 | 4.5 | 0.237 | 4.026 | 10.79 | 0.337 | 3.826 | 14.98 | A53-B / A106-B
5 | 5.563 | 0.258 | 5.047 | 14.62 | 0.375 | 4.813 | 20.78 | A53-B / A106-B
6 | 6.625 | 0.28 | 6.065 | 18.97 | 0.432 | 5.761 | 28.57 | A53-B / A106-B
8 | 8.625 | 0.322 | 7.981 | 28.55 | 0.5 | 7.625 | 43.39 | A53-B / A106-B
10 | 10.75 | 0.365 | 10.02 | 40.48 | 0.5 | 9.75 | 54.74 | A53-B / A106-B
12 | 12.75 | 0.406 | 11.938 | 53.52 | 0.5 | 11.75 | 65.42 | A53-B / A106-B
PIPE WEIGHT CALCULATOR (Pick NPS + Schedule, enter length)
NPS: | 2 | Schedule: | SCH 40
Length (ft): | 10
Wt/ft (lb/ft):
Total Weight (lbs):

## Materials
STRUCTURAL STEEL MATERIAL GRADES (Quick Reference)
Grade | Fy (ksi) | Fu (ksi) | Typical Use | Weldability | Notes
A36 | 36 | 58-80 | Plates, angles, channels, misc steel | Good | E70xx; most common general grade
A572 Gr50 | 50 | 65 | W-shapes, beams, columns | Good | E70xx; higher strength than A36
A992 | 50+ | 65 | W-shapes (modern standard) | Good | Max Fy/Fu = 0.85; preferred for W-shapes
A500 Gr B | 46 | 58 | HSS rectangular/square | Good | E70xx; check heat properties
A500 Gr C | 50 | 62 | HSS rectangular/square | Good | Higher strength HSS option
A53-B | 35 | 60 | Structural pipe | Fair | Preheat for heavy walls; E7018
A106-B | 35 | 60 | High-temp service pipe | Fair | Common in O&G process piping; E7018
A108 | Var. | Var. | Bolts, studs, shafting | N/A | Not for primary structural welding
WELDING ELECTRODE QUICK REFERENCE
Electrode | Min Tensile | Process | Typical Use | Notes
E7018 | 70 | SMAW (Stick) | Primary structural; low hydrogen | Preferred for A53/A106 pipe
E70XX | 70 | SMAW (Stick) | General structural fillet/groove | Matches A36/A572/A992
E6010 | 62 | SMAW (Stick) | Root pass, field welding | DC+; burns through rust/scale
E6013 | 62 | SMAW (Stick) | Light fab, sheet metal | AC or DC; easy for beginners
ER70S-6 | 70 | GMAW (MIG) | Shop fillet welds, general fab | CO2 or 75/25 Ar/CO2 gas
E71T-1 | 70 | FCAW | High-production fillet welds | CO2 shielding; fast deposition
• E70xx electrodes match A36, A572, A992 (tensile ≥ 70 ksi)
• Use E7018 (low hydrogen) on A53-B / A106-B pipe per most WPS
• Always verify material grade from Mill Test Report (MTR)
• A992 is current standard for W-shapes
• A500 Gr B/C is used for HSS — verify per PO

## Handrail
HANDRAIL — OSHA & SHOP STANDARDS
Item | Value / Spec | Code Reference
Top Rail Height | 42" nominal (min 42") | OSHA 1910.29
Mid Rail Height | 21" (midpoint) | Required when opening > 19"
Toeboard Height | 3-1/2" min | Prevents tools/objects from rolling off
Max Post Spacing | 8'-0" typical | Check project spec
Top Rail Min Strength | 200 lbs | OSHA load requirement
Mid Rail Min Strength | 150 lbs | OSHA load requirement
Gate Opening Clear | 22" min | Self-closing at stair openings
COMPONENT REFERENCE
Component | Mat'l Opt 1 | Mat'l Opt 2 | Typical Size | Notes
Top Rail | Pipe | Angle | 1-1/2" SCH 40 / L1.5x1.5x3/16 | 1.5" pipe OD = 1.900"
Mid Rail | Pipe | Angle | 1-1/2" SCH 40 / L1.5x1.5x3/16 | Same as top rail
Post | Pipe | Sq. Tube | 1-1/2" SCH 40 / HSS2x2x3/16 | Weld to base plate
Base Plate | A36 Plate |  | 4"x4"x3/8" typical | 2x 1/2" dia anchor bolts
Kickplate | Flat Bar | Plate | 1/4" x 4" Flat Bar | Tack both edges
Return End | Pipe |  | 180° return, same size | Or cap plate w/ nosing
Gate Post | Sq. Tube |  | HSS2x2x1/4 | Heavier to handle gate load
HANDRAIL RUN CALCULATOR (Yellow = input, Green = result)
Total Run Length (ft): | 20
Post Spacing (ft, ≤8): | 6
Number of Posts:
Top Rail Length (ft): |  | (+2 for returns)
Mid Rail Length (ft): |  | (+2 for returns)

## Pipe Supports
PIPE SUPPORT TYPE REFERENCE (O&G / Chemical)
Support Type | Description | Pipe Size | Base Plate | Material | Shop Notes
Dummy Leg / Shoe | Welded to pipe; sits on structure | 2"-24" | 6x6x1/2 min | A36 | Most common O&G support
Guide | Allows axial travel; restricts lateral | 2"-24" | 6x8x1/2 | A36 | Gap = OD + 1/2" typ
Anchor (Fixed) | Fully fixed — all loads/moments | 2"-16" | 10x10x3/4 | A36 | Gussets usually required
Rod Hanger | Threaded rod from above | 1/2"-12" | N/A | A307/A36 | Check engagement length
U-Bolt | Bolted clamp; wraps pipe | 1"-12" | N/A | A36/SS | Order by pipe NPS
Pipe Clamp | Bolted clamshell; MSS SP-58 | 1/2"-36" | N/A | A36/SS | Type 1/4/24/36 common
Spring Hanger | Variable/constant-effort spring | Per mfr | N/A | Mfr std | Specify load, travel
Saddle | Supports insulated pipe from below | 2"-24" | Per design | A36 | Insulation insert required
Trunnion | Large pipe; pin-mounted to structure | 12"-48" | Heavy plate | A36 | Requires stress analysis
DUMMY LEG / SHOE SIZING GUIDE (Typical — Verify w/ Engineer)
Pipe NPS | Pipe OD | Shoe Ht | BP Width | BP Length | BP Thickness | Stiffener?
2 | 2.375 | 6" | 5" | 6" | 3/8" | No
3 | 3.5 | 6" | 6" | 7" | 3/8" | No
4 | 4.5 | 6" | 7" | 8" | 3/8" | No
6 | 6.625 | 6" | 8" | 10" | 1/2" | Consult
8 | 8.625 | 8" | 10" | 12" | 1/2" | Yes
10 | 10.75 | 8" | 12" | 14" | 1/2" | Yes
12 | 12.75 | 8" | 12" | 14" | 3/4" | Yes
14 | 14 | 10" | 14" | 16" | 3/4" | Yes
16 | 16 | 10" | 16" | 18" | 3/4" | Yes
SUPPORT DETAIL LOG (Fill in as you detail — dropdown in column D)
Tag | Line # | NPS | Support Type | Elev (ft) | Material | Base Plate | Gusset? | Notes

## Platforms
GRATING REFERENCE
Type | Designation | Bar Size | Panel Sizes | Wt (lb/ft²) | Notes
Bar Grating (welded) | 19-W-4 | 1-3/16" x 3/16" | 24"/36"/48" wide, up to 20' | 11 | Most common O&G spec
Bar Grating (welded) | 15-W-4 | 15/16" x 3/16" | 24"/36"/48" wide | 9 | Lighter applications
Bar Grating (swaged) | 19-W-4 | 1-3/16" x 3/16" | 24"/36"/48" wide | 11 | No welds; cold-locked
Checkered Plate | 3/16" | N/A | 48x96, 60x120 | 8.25 | Verify pattern add'l wt
Checkered Plate | 1/4" | N/A | 48x96, 60x120 | 10.6
Checkered Plate | 3/8" | N/A | 48x96, 60x120 | 15.6 | Heavy traffic
STRUCTURAL MEMBER REFERENCE
Member | Typical Size | Material | Max Span | Notes
Floor Beam | W8x18 or W8x24 | A992/A572 | 12-16 ft | Typical for 50 psf
Header / Rim | W10x22 or C10x20 | A992/A572 | Varies | Perimeter support
Knee Brace | L3x3x3/8 or HSS3x3x3/16 | A36/A500 | N/A | 45° typical
Column | HSS4x4x1/4 or W6x15 | A500/A992 | 10-16 H | Base plate required
Handrail Post | 1-1/2" SCH 40 Pipe | A53-B | 8'-0" max | 42" above FF
Stair Stringer | C10x20 or C12x20.7 | A36/A572 | Varies | Slope per design
Gusset Plate | 3/8" plate typical | A36 | N/A | Size per loading
DESIGN NOTES & SHOP STANDARDS
Item | Standard Value | Notes
Design Live Load | 50 psf typical | ASCE 7 minimum
Grating Direction | Perp. to floor beams | Bearing bar across span
Grating Fasteners | Saddle clips 24" o.c. | 4 clips min per panel edge
Drain Hole | 1" dia per 100 sq ft | At low point
Stair Width Min | 22" clear | 36" preferred for O&G
Tread Depth | 11" min | Nosing included
Riser Height | 7" max | Uniform for full flight
Nosing | L1.25x1.25x1/8 angle | Tack weld both legs
Safety Yellow Paint | All leading edges | Kickplates, nosings
Overhead Clearance | 7'-0" min | OSHA walkway
PLATFORM BILL OF MATERIALS (Fill in — Total Wt auto-calcs)
Mark | Description | Material | Size | Length (ft) | Qty | Wt/ea (lbs) | Total Wt
GRAND TOTAL (lbs):

## Bolts
BOLT & ANCHOR ROD GRADES (AISC / ASTM)
Spec | Grade | Fy (ksi) | Fu (ksi) | Shear (ksi) | Tension (ksi) | Notes
A307 | Low carbon | N/A | 60 | 27.0 | 45.0 | Non-structural; anchor bolts, light connections
A325 | Med carbon | 92 | 120 | 54.0 | 90.0 | Standard structural bolt; most common
A490 | Alloy steel | 130 | 150 | 67.5 | 112.5 | High-strength; heavier connections
F1554 Gr36 | Low carbon | 36 | 58 | N/A | N/A | Anchor rods; weldable
F1554 Gr55 | Med carbon | 55 | 75 | N/A | N/A | Anchor rods; higher strength
F1554 Gr105 | Alloy | 105 | 125 | N/A | N/A | Anchor rods; heavy equipment
A36 Threaded | Low carbon | 36 | 58 | N/A | N/A | All-thread rod; misc bracing/hangers
STANDARD HOLE SIZES (AISC Table J3.3)
Bolt Dia | STD Hole | OVS Hole | SSLOT Width | SSLOT Length | LSLOT Width | LSLOT Length
1/2" | 9/16" | 5/8" | 9/16" | 11/16" | 9/16" | 1-1/4"
5/8" | 11/16" | 13/16" | 11/16" | 7/8" | 11/16" | 1-9/16"
3/4" | 13/16" | 15/16" | 13/16" | 1" | 13/16" | 1-7/8"
7/8" | 15/16" | 1-1/16" | 15/16" | 1-1/8" | 15/16" | 2-3/16"
1" | 1-1/16" | 1-1/4" | 1-1/16" | 1-5/16" | 1-1/16" | 2-1/2"
1-1/8" | 1-3/16" | 1-3/8" | 1-3/16" | 1-7/16" | 1-3/16" | 2-13/16"
1-1/4" | 1-5/16" | 1-1/2" | 1-5/16" | 1-9/16" | 1-5/16" | 3-1/8"
MIN EDGE DISTANCE & BOLT SPACING (AISC Table J3.4)
Bolt Dia | Min Edge (sheared) | Min Edge (rolled/saw) | Min Spacing (3x dia)
1/2" | 7/8" | 3/4" | 1-1/2"
5/8" | 1-1/8" | 7/8" | 1-7/8"
3/4" | 1-1/4" | 1" | 2-1/4"
7/8" | 1-1/2" | 1-1/8" | 2-5/8"
1" | 1-3/4" | 1-1/4" | 3"
1-1/8" | 2" | 1-1/2" | 3-3/8"
1-1/4" | 2-1/4" | 1-5/8" | 3-3/4"
APPROXIMATE SNUG-TIGHT TORQUE (Reference only — follow approved ITP)
Bolt Dia |  | Grip Range | A325 Torque (ft-lbs) | A490 Torque (ft-lbs)
1/2" |  | 3/16" – 1" | 85 | 107
5/8" |  | 3/16" – 1" | 170 | 212
3/4" |  | 1/4" – 1-1/2" | 300 | 375
7/8" |  | 1/4" – 2" | 490 | 612
1" |  | 1/4" – 2" | 730 | 912
1-1/8" |  | 3/8" – 2" | 1050 | 1312
1-1/4" |  | 3/8" – 2" | 1460 | 1825
• STD = Standard hole ¦ OVS = Oversized ¦ SSLOT = Short-slot ¦ LSLOT = Long-slot
• A325 and A490 are now superseded by ASTM F3125 Gr A325/A490 — same dimensions/strengths
• Min spacing = 2-2/3 × bolt dia (preferred 3×); min edge = per table above
• For slip-critical connections use Class A or B faying surface — see engineer
• Torque values are approximate — always follow the project Inspection & Test Plan (ITP)
• F1554 anchor rods: embed length = 12× dia minimum unless engineer specifies otherwise